## Sheet1
MAIN HOUSE PANEL BOX
LOAD | EQUIPMENT | POLES | WIRE | AMPS |  |  | AMPS | WIRE | POLE | EQUIPMENT | LOAD
10000 | A/C HEAT UNIT NO.1 | 2 | 6 | 60 | 1 | 2 | 20 | 12 | 1 | DISHWASHER | 1500
[5 empty] | 3 | 4 | 20 | 12 | 1 | DISPOSAL | 900
1500 | SMALL APPL. (GFI) | 1 | 12 | 20 | 5 | 6 | 20 | 12 | 1 | WASHER | 1500
1500 | SMALL APPL. (GFI) | 1 | 12 | 20 | 7 | 8 | 20 | 12 | 1 | GARAGE DOOR OPEN | 600
830 | REF. | 1 | 12 | 20 | 9 | 10 | 20 | 6 | 2 | A/C HEAT UNIT NO.2 | 10000
| Spare |  |  |  | 11 | 12
| Spare |  |  |  | 13 | 14 | 60 | 6 | 2 | CAR CHARGER | 6000
5000 | DRYER | 1 | 10 | 30 | 15 | 16
4500 | WATER HEATER | 2 | 10 | 25 | 17 | 18 |  |  |  | General Lighting & Recept.
[5 empty] | 19 | 20 |  |  |  | General Lighting & Recept.
2000 | POOL EQUIPMENT | 2 | 6 | 20 | 21 | 22 | 50 | 6 | 2 | Range | 8500
[5 empty] | 23 | 24
13330 | LOAD LEFT SIDE | [8 empty] | LOAD RIGHT SIDE | 13000
TOTALS
| GENERAL LIGHTING | 3000 | @ | 3 | w |  | 9000
| NAME PLATE RATING | [5 empty] | 26330
| TOTAL WATTS LESS A/C | [5 empty] | 35330 |  |  | REPRESENTS CONT LOAD
| FIRST 10000 W @ 100% | [5 empty] | 10000
| REMAINER @ 40% | [5 empty] | 10132
| CONTINUOUS LOAD - A/C, POOL, CHARGER | [5 empty] | 28000
| TOTAL PANEL LOAD |  |  | 48132 | watts | / | 240 V |  | 200.55
| MIN PANEL BOX SIZE |  |  | 250 | amp | Licensed Electrician to verify all loads and modify if needed.